## Slide 1
SHORT-TERM ELECTRICITY MARKET SIMULATION
The Spanish Power System
A multi-stage market chain feeding an AC optimal power flow redispatch
Model · Case study · Results
Peninsular transmission grid — 1,236 buses · 2,345 branches · 2,035 generating units
Two representative days: 8 July 2024 (summer) and 2 December 2024 (winter)
Generated from results_plots.ipynb · June 2026

## Slide 2
AGENDA
What this deck covers
1
The model — a multi-stage short-term market chain
Day-ahead clearing → three intraday gates → AC OPF redispatch
2
The case — the Spanish peninsular grid
Full transmission network, two contrasting demand days, cross-border ties
3
Methodology
Copper-plate economic dispatch, Bellman-coupled hydro, AC redispatch with reactive realism
4
Dispatch results
Fuel mix, merit order, capacity utilisation, hourly profiles, system prices
5
Network & reactive results
Branch loading & congestion, voltage profile, reactive procurement, feasibility
Spanish Power System · Market-Chain + AC OPF
1

## Slide 3
PART I
The Model
A multi-stage representation of the short-term electricity market
Spanish Power System · Market-Chain + AC OPF
2

## Slide 4
MODEL · OVERVIEW
A market chain, not a single optimisation
Real electricity markets clear in sequential stages. The model reproduces that chain: a day-ahead schedule is progressively revised by intraday gates, then made physically feasible on the AC network by a redispatch step.
DAY-AHEAD
Copper-plate economic dispatch
ID2
Intraday adjustment gate
ID3
Intraday gate (hours 12–23)
CID
Continuous intraday
REDISPATCH
AC OPF on the real network
Each stage hands its schedule to the next as a warm-start / anchor
• Stages 1–4 are copper-plate (system-wide power balance only, no network) and share one Bellman-coupled 24-hour formulation — they differ only in the demand scaling and what is frozen.
• Intraday gates are adjustment markets: they re-clear cost first, then minimise total movement from the previous schedule (lexicographic tie-break) so units only move when there is a real reason.
• The final stage is a full AC optimal power flow that enforces the physical grid — line ratings, voltages and reactive power — by redispatching only the units that are allowed to move.
Spanish Power System · Market-Chain + AC OPF
3

## Slide 5
MODEL · DAY-AHEAD
Stage 1 — Day-ahead economic dispatch
• Copper-plate dispatch over all 24 hours at once
  – One system-wide balance per hour: Σ generation = Σ load
  – No network, voltage or reactive constraints at this stage
• Reservoir hydro coupled across the day
  – Full Bellman cost-to-go (water value) links the 24 hours so stored water is allocated to the most valuable hours
  – Cost of reservoir output comes entirely from the future-value term
• Merit-order clearing
  – Zero-cost renewables (wind, solar, run-of-river) dispatched first, then nuclear, hydro, gas …
  – Cross-border imports enter as fixed injections; slack & load-shed units stand by
• Solves as a linear program in ~1–5 s per day
Objective (per day)
min Σₕ Σ_g c_g · p_{g,h}
+ θ_future(water)
subject to
Σ_g p_{g,h} = load_h ∀h
p_g^min ≤ p_{g,h} ≤ p_g^max
reservoir storage balance
+ Bellman value cuts
Output → day-ahead schedule,
the anchor for the intraday gates
Spanish Power System · Market-Chain + AC OPF
4

## Slide 6
MODEL · INTRADAY
Stages 2–4 — Intraday adjustment gates
The intraday gates (ID2 → ID3 → CID) refine the day-ahead schedule as the demand forecast is updated. Each gate is an adjustment market solved lexicographically, not a fresh clearing.
Step 1 — minimise dispatch cost
Re-clear the merit order for the updated demand — cheapest feasible units, as in any market.
Step 2 — minimise movement
Among all cost-optimal solutions, pick the one closest to the previous gate: min Σ (Δ↑ + Δ↓). Removes cost-degenerate reshuffles that move units for no net reason.
• Anchoring chain: ID2 anchors to day-ahead; ID3 retrades only hours 12–23 (0–11 carry over); CID rolls gate-by-gate, anchoring each hour to the latest market view.
• Nuclear is frozen at its day-ahead value from ID2 onward (baseload does not chase intraday signals).
• All gates reuse the same Bellman-coupled 24-hour reservoir formulation as the day-ahead stage.
• The CID schedule is the realised market dispatch that the AC redispatch must make grid-feasible.
Spanish Power System · Market-Chain + AC OPF
5

## Slide 7
MODEL · REDISPATCH
Stage 5 — AC OPF redispatch
• Full non-linear AC optimal power flow
  – Enforces the real grid: line thermal ratings, bus voltage band, and AC power-balance (active + reactive) at every bus.
  – Warm-started from the CID market schedule; objective keeps the dispatch as close to it as possible while restoring feasibility.
• Who can move?
  – Frozen at market value: Nuclear, run-of-river Hydro, Biomass (pmin = pmax).
  – Free to redispatch: Gas, Coal, Oil, reservoir & pumped hydro, and curtailable Wind / Solar.
• Reactive & voltage realism
  – Shunt reactors (REE fleet), full π-model line charging, per-fuel generator reactive capability, and an AVR voltage band.
• Solved with Ipopt + HSL/MA57 — every hour reaches a locally optimal AC solution.
Redispatch objective
min base cost
+ w · Σ (P_g − P_g^CID)²
subject to
AC power balance (P & Q)
|S_line| ≤ rating
0.95 ≤ V ≤ 1.05 pu
gen P–Q capability limits
frozen units: P = P^CID
w = anchor weight tying the
solution to the market result
Spanish Power System · Market-Chain + AC OPF
6

## Slide 8
MODEL · AC REALISM
Methodology deep-dive — a physically realistic AC OPF
A pure loss-minimising AC OPF is physically naïve: it pushes reactive power onto generators and rails almost every bus up to the upper voltage limit. Four mechanisms — each calibrated to the real Spanish grid — restore realistic reactive flows and voltages.
1 · Line charging (π-model)
Every AC line is a full π-model. ~48,000 km of EHV generate ≈21 GVAr of charging at 1.0 pu (≈17 GVAr from 400 kV alone) that must be absorbed.
2 · Shunt reactors
REE's installed peninsular reactor fleet (15.5 GVAr) is placed on buses to soak up that charging — exactly what the real operator does.
3 · Generator reactive capability
Technology-specific P–Q limits: a capability circle for synchronous machines, a grid-code cap for inverter-based wind & solar.
4 · AVR voltage band
Synchronous machines hold their bus to an AVR setpoint near nominal, pulling the voltage profile off the upper rail.
Spanish Power System · Market-Chain + AC OPF
7

## Slide 9
METHODOLOGY · REACTORS
Shunt reactors — compensating EHV line charging
• The problem
  – Every line is a full π-model with charging susceptance. Across ~48,000 km of 400/220 kV this generates ≈21 GVAr at nominal voltage (≈17 GVAr from 400 kV alone).
  – With nothing to absorb it, the OPF dumps that reactive onto generators and voltages ride the upper band — physically the job of shunt reactors.
  – Modelled as proper shunt elements with negative susceptance (bs < 0, inductive). PowerModels ignores bus-level bs, so they must live in the shunt component.
• Disaggregation
  – The aggregate fleet is spread to buses in proportion to the AC line charging connected at each bus, within each voltage group (400 kV vs ≤220 kV).
  – Per-bus result cached in Data/reactors.csv — fixed and reproducible across runs.
  – Config knob in_service_pct scales the energised fraction — emulating switched reactors without turning the AC OPF into a mixed-integer problem.
Installed peninsular fleet
REE Boletín Mensual, diciembre 2024
Voltage group
Installed
Units
400 kV
11,750 MVAr
80
≤ 220 kV
3,722 MVAr
55
Peninsular total
15,472 MVAr
135
≈ 80% of the EHV line charging is compensated — consistent with the standard EHV planning rule. Balearic & Canary systems excluded (non-synchronous).
config.toml
[reactors]
enabled = true
in_service_pct = 100.0
Spanish Power System · Market-Chain + AC OPF
8

## Slide 10
METHODOLOGY · REACTIVE
Generator reactive capability — per technology
Reactive limits are technology-specific and enforced in every redispatch stage (hour-by-hour anchored solves and the Bellman-coupled multi-hour solve).
Synchronous machines
Nuclear · Gas · Coal · Oil · Biomass · Hydro
P² + Q² ≤ S_rated²
S_rated = installed MVA / 0.90
• An apparent-power capability circle, sized on installed nameplate MVA.
• A machine's MVA rating is fixed regardless of output, so it can supply reactive even at low MW.
• Convex (second-order cone) → Ipopt solves it as an NLP. Replaces the old ±Pmax box that allowed PF 0.707 at full output.
Inverter-based units
Wind · Solar
|Q| ≤ tan(acos(0.95)) · P
• A grid-code reactive cap tied to actual output, not nameplate.
• Sizing on actual P stops a heavily-derated farm (e.g. 38 of 100 MW) parking at a very low PF.
• An installed-MVA circle for renewables gave low-availability farms huge reactive headroom — the per-fuel split is what fixes it.
config.toml [generators]
apparent_power_limit = true rated_power_factor = 0.90 renewable_power_factor = 0.95
Spanish Power System · Market-Chain + AC OPF
9

## Slide 11
METHODOLOGY · VOLTAGE
Voltage realism — load reactive & AVR regulation
Load reactive demand
qd = pd · tan(acos(power_factor))
• power_factor is the net PF the transmission grid sees; distribution-level correction is assumed already applied below the model boundary.
• Default 1.0 ⇒ active-only load, leaving all the line charging for the reactors to absorb; a lower PF lets the load soak up much of it (~11.5 GVAr at 0.95). Tune with reactors together.
AVR voltage band
• A loss-minimising OPF rails voltages to vmax (higher V ⇒ lower current ⇒ lower losses).
• Real synchronous machines are AVR-regulated to a setpoint: AVR buses (slack + synchronous-hosting) are held to a tight 0.98–1.03 band.
• Renewable-only & load buses keep the wider ±0.05 — a derated farm can't firmly hold a setpoint.
Effect on the profile
full fleet, 48 h
Mean bus voltage
1.037 → 1.023 pu
Buses sitting at vmax
7.8% → 0.9%
config.toml [network]
voltage_band = 0.05 gen_bus_voltage_control = true
gen_bus_vmin = 0.98 gen_bus_vmax = 1.03
Spanish Power System · Market-Chain + AC OPF
10

## Slide 12
PART II
The Case
The Spanish peninsular transmission system on two contrasting days
Spanish Power System · Market-Chain + AC OPF
11

## Slide 13
CASE · NETWORK
The Spanish peninsular grid
1,236
buses
2,345
AC branches
2,035
generating units
48
hourly snapshots
• Geographic transmission model of peninsular Spain at 400 / 220 / 132 kV and below, built from REE network data — every line is a full π-model with charging susceptance.
• EHV scale: ~48,000 km of lines carry roughly 21 GVAr of line charging at 1.0 pu (≈17 GVAr from the 400 kV layer alone) — reactive management is a first-order concern.
• Shunt reactors from the REE December-2024 fleet (≈11.75 GVAr at 400 kV, ≈3.72 GVAr at ≤220 kV) are placed on buses in proportion to connected line charging.
• Cross-border AC ties to France and Portugal (13 lines, no HVDC) inject the market-cleared exchange as fixed boundary injections — ~1.9 GW of net imports on average.
Spanish Power System · Market-Chain + AC OPF
12

## Slide 14
CASE · DEMAND
Two representative days
Attribute
8 July 2024 · summer
2 December 2024 · winter
Season
Summer
Winter
Peak demand
39.4 GW
33.9 GW
Minimum demand
21.3 GW
21.4 GW
Avg. system cost
≈ 147 k€/h
≈ 464 k€/h
Dominant flexibility
Solar midday peak
Gas-heavy evenings
Hours solved (AC)
24 / 24
24 / 24
Two days chosen to bracket the system: a high-renewable summer day with a pronounced solar peak, and a tighter winter day where thermal generation carries the evening — driving the ≈3× higher system cost.
Spanish Power System · Market-Chain + AC OPF
13

## Slide 15
PART III
The Results
Dispatch, prices, network loading, voltages and reactive power
Spanish Power System · Market-Chain + AC OPF
14

## Slide 16
RESULTS · DISPATCH
Generation mix & average dispatch
Key takeaways
• Hydro is the workhorse of both days (≈10 GW average), followed by solar (≈6.7 GW) and nuclear baseload (≈5.7 GW).
• Wind contributes ≈4.9 GW on average; gas (≈1.4 GW) fills the residual and sets the price at the margin.
• Coal and oil sit essentially idle — pushed out of the merit order by cheap renewables and hydro.
Spanish Power System · Market-Chain + AC OPF
15

## Slide 17
RESULTS · DISPATCH
Installed capacity vs. utilisation
Key takeaways
• Gas has the largest installed fleet (≈28 GW) but runs at low utilisation — a peaking / balancing role.
• Solar (33 GW) and wind (30 GW) dominate capacity; their average output reflects availability, not scarcity.
• Nuclear runs close to its ≈7.4 GW nameplate — the firm baseload of the system.
Spanish Power System · Market-Chain + AC OPF
16

## Slide 18
RESULTS · ECONOMICS
Merit order — dispatch vs. marginal cost
Key takeaways
• Zero-marginal-cost renewables and hydro are dispatched first and carry the bulk of the energy.
• Dispatch falls away as marginal cost rises — the classic merit-order staircase.
• Gas units cluster at the expensive, lightly-loaded end: on only when the grid needs them.
Spanish Power System · Market-Chain + AC OPF
17

## Slide 19
RESULTS · DISPATCH
Top dispatched generators
Key takeaways
• The most-dispatched units are large hydro and nuclear stations running near capacity.
• High average utilisation among the top units confirms a stable, baseload-anchored dispatch.
• No single thermal unit dominates — flexibility is spread across the gas fleet.
Spanish Power System · Market-Chain + AC OPF
18

## Slide 20
RESULTS · PROFILES
Hourly generation mix — both days
Key takeaways
• Summer (left): a strong midday solar bulge displaces gas and even backs nuclear down at the peak.
• Winter (right): no solar shoulder — hydro and gas shape the evening ramp, lifting system cost.
• Demand is met in every hour of both days with the real fleet (post-redispatch).
Spanish Power System · Market-Chain + AC OPF
19

## Slide 21
RESULTS · ECONOMICS
Hourly system cost & price
Key takeaways
• System price tracks the marginal technology: low when solar/hydro clear, high in thermal-heavy hours.
• The winter day is markedly more expensive (≈464 k€/h vs ≈147 k€/h average) — more gas at the margin.
• Price peaks align with the morning and evening demand ramps.
Spanish Power System · Market-Chain + AC OPF
20

## Slide 22
RESULTS · FLEXIBILITY
Hour-to-hour dispatch changes
Key takeaways
• Bars show each technology's hour-on-hour change; the line is the net load change.
• Hydro and gas provide the bulk of the ramping flexibility, mirroring the demand curve.
• Solar swings drive the largest mid-day movements on the summer day.
Spanish Power System · Market-Chain + AC OPF
21

## Slide 23
RESULTS · ADEQUACY
Slack-bus generation — capacity adequacy
Key takeaways
• The slack unit (priced at 1,000× base) only runs if the real fleet cannot meet demand.
• Dispatch stays negligible across all 48 hours — no genuine capacity shortfall.
• Confirms the modelled fleet plus imports is adequate for both days.
Spanish Power System · Market-Chain + AC OPF
22

## Slide 24
RESULTS · NETWORK
Branch loading & congestion
Key takeaways
• Across 48 hours and 2,345 branches, mean loading is only ≈14% — the grid is lightly loaded on average.
• Just ≈0.3% of branch-hours exceed 90% loading; congestion is rare and localised.
• A handful of branches are persistently the binding constraints that the redispatch works around.
Spanish Power System · Market-Chain + AC OPF
23

## Slide 25
RESULTS · NETWORK
Bus voltage profile
Key takeaways
• Every bus in every hour stays inside the 0.95–1.05 pu band — no violations.
• Mean voltage ≈1.024 pu: the AC OPF holds a healthy, slightly-high profile.
• Reactor switching and reactive procurement keep EHV charging in check.
Spanish Power System · Market-Chain + AC OPF
24

## Slide 26
RESULTS · NETWORK
Voltage map — mean & worst-case
Key takeaways
• Left: mean voltage per bus; right: worst-case minimum across all solved hours.
• Voltages stay comfortably within limits across the whole peninsula.
• No regional pocket drops below 0.95 pu even in the worst hour.
Spanish Power System · Market-Chain + AC OPF
25

## Slide 27
RESULTS · REACTIVE
Reactive power procurement
Key takeaways
• Synchronous hydro and gas units supply most of the reactive support, within their P–Q capability circles.
• Inverter-based wind and solar contribute bounded reactive tied to their actual output.
• Per-fuel power factors stay realistic — no unit is pushed to an implausible operating point.
Spanish Power System · Market-Chain + AC OPF
26

## Slide 28
RESULTS · REACTIVE
Reactive branch flows
Key takeaways
• Most branches carry predominantly active power (high power factor) — the intended design point.
• Reactive flows concentrate where line charging and reactor compensation interact.
• The π-model line charging and shunt reactors net out to a stable reactive balance.
Spanish Power System · Market-Chain + AC OPF
27

## Slide 29
RESULTS · ADEQUACY
Feasibility & load shedding
Key takeaways
• A load-shedding unit (Value of Lost Load = 10,000 €/MWh) sits at every load bus as a safety valve.
• Zero load shedding was dispatched across all 48 hours.
• Raising the line-rating factor from 70% to 80% was enough to make every hour AC-feasible.
Spanish Power System · Market-Chain + AC OPF
28

## Slide 30
SUMMARY
Results at a glance
48 / 48
hours solved to AC optimality
0 MW
load shed — fully adequate
100%
bus-hours within 0.95–1.05 pu
~14%
mean branch loading
~0.3%
branch-hours congested (>90%)
~1.9 GW
average net cross-border imports
• The market chain produces a realistic merit-order dispatch; the AC redispatch makes it physically feasible with minimal intervention.
• Summer is renewable-rich and cheap; winter leans on gas and costs roughly three times as much per hour.
• Network mismatch in the summary equals AC losses (≈0.2–1.4 GW, ≤4% of load) — not an imbalance.
Spanish Power System · Market-Chain + AC OPF
29

## Slide 31
SUMMARY
A market-faithful, network-feasible simulation
• Day-ahead → intraday gates → AC OPF redispatch reproduces the Spanish short-term market chain end-to-end.
• Two contrasting days on the full peninsular grid solve to AC optimality with no load shedding and no voltage violations.
• All figures reproducible from results_plots.ipynb over the results/ CSVs.